SLN 2_Annex1 – Sampling Request

This form should be used by SLP and emailed to self.lay@dwrcymru.com to inform DCWW that they intend to make a routine mains connections. It should be submitted 5 working days in advance of the date on which the self-laid mains are to be pressure tested and chlorinated.

SECTION 1 – Contact details

Scheme name: __________________________________________________________________

Self-lay Provider name (SLP): ______________________________________________________

Contact name: __________________________________________________________________

Contact telephone number (preferably mobile):_________________________________________

Date sent to DCWW:    D    D   /  M   M   /   Y   Y   Y    Y

SECTION 2 – Job number / Site address

Dwr Cymru Welsh Water Scheme Number

Site address: ___________________________________________________________________

_________________________________________ Postcode_____________________________

Plan enclosed of sampling points?  	Yes – This must be provided

SECTION 3 – Pressure Test Details

All tests may be witnessed by DCWW and the appropriate test certificate handed to the DCWW      responsible officer. DCWW form SLN1 is to be used to notify the date of both main laying and pressure testing and chlorination.

Date of pressure test certificate handover to DCWW: 	D    D   /  M   M   /   Y   Y   Y    Y

SECTION 4 – Chlorination details

All fittings are to be sprayed on assembly at 1000 mg/l. Swab to prepare for disinfection and flush before full chlorination which is to be carried out by injection at 20mg/l sodium hypochlorite and left to stand for at least 16hours. Flush to discharge chlorine following appropriate de-chlorination at the point of discharge. The final residual shall be no greater than the residual in the existing supply.

Date of Full Chlorination      D    D   /  M   M   /   Y    Y    Y    Y

Chlorine residual after chlorination______________ppm   Contact period_______________________hrs/mins

Volume of water used for flushing_______________m3   Quantity of sodium ipochlorite_______________litres

Chlorine residual after standing time_____________ppm   Date of flushing   D   D  /   M  M  /   Y   Y    Y   Y

Chlorine residual after flushing______________ppm

SECTION 5 – Onsite taste, odour and clarity

Taste: 		Satisfactory: 		Yes 		No

Odour: 		Satisfactory: 		Yes 		No

Clarity: 		Satisfactory: 		Yes 		No

SECTION 6 – Declaration

I CERTIFY THAT THE ABOVE HAS BEEN CARRIED OUT IN ACCORDANCE WITH THE RELEVANT

WRc GUIDELINES AND DCWW WORKING PRACTICES.

Chlorinator’s company: __________________________________________________________

Chlorinator’s printed name: _______________________________________________________

Chlorinator’s signature: _________________________________________ Date: ____________

SECTION 7 – STL Sampling Details (Sampling to be taken within 3 working days of request)

Date of Sampling: ______________ Time of sampling: __________ Lab Ref No(s): ___________

DCWW / UUOS WATER QUALITY DEPARTMENT

Sampler’s Name (Print): ______________________ Sampler’s Signature: ___________________

Bacteriological results    Satisfactory		Unsatisfactory		Results:  TC         EC

If unsatisfactory specify action to be taken:_____________________________________________________

Chemical results	     Satisfactory	Unsatisfactory		Resampling required:  Yes    No

Specify action to be taken:__________________________________________________________________

Printed name + Signature:__________________________________________________Date____________